## Checkbox
ASD WAREHOUSE DESIGN CONSIDERATIONS
The following greyscale table is provided to allow the designer/specifier to consider several questions regarding the overall aspirating detection system design within a warehousing facility. The emphasis and conclusions of the various questions guide the designer/specifier to a selection of five different detection schemes. Scheme 1 to scheme 5 contain increasing amounts of aspirating system detection points to protect the warehouse facility more comprehensively.
One of the five boxes underneath each of the highlighted questions may be used to confirm the degree of risk/consideration for the particular warehouse facilty. By way of weighting the results of all the questions should suggest one of the five schemes detailed below the questions.
Low | Criticality of the warehouse to the business |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Consequences of the loss |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
High | Occupancy |  |  | Low
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Ceiling height |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Flammability, fire load and risk of fire spread |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Probability of ignition |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Detection challenges (airflows, obstacles, temperature gradient) |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
High | Response capabilities |  |  | Low
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
Low | Provision of automatic suppression (sprinklers) |  |  | High
FALSE | FALSE | TRUE | FALSE | FALSE | 1
OK
0 | 0 | 9 | 0 | 0
| Total | 540
180 | Between 181 & 360 | Between 361 & 540 | Between 541 & 719 | 720 +
Scheme 1 Ceiling only normal coverage (see table 3) | Scheme 2 Ceiling only strategically positioned relative to the racking | Scheme 3 Ceiling + top of rack detection | Scheme 4 Ceiling + multi-level in rack detection | Scheme 5 Ceiling + localised multi-level in rack
FALSE | FALSE | TRUE | FALSE | FALSE

## Slider
ASD WAREHOUSE DESIGN CONSIDERATIONS
The following greyscale table is provided to allow the designer/specifier to consider several questions regarding the overall aspirating detection system design within a warehousing facility. The emphasis and conclusions of the various questions guide the designer/specifier to a selection of five different detection schemes. Scheme 1 to scheme 5 contain increasing amounts of aspirating system detection points to protect the warehouse facility more comprehensively.
One of the five boxes underneath each of the highlighted questions may be used to confirm the degree of risk/consideration for the particular warehouse facilty. By way of weighting the results of all the questions should suggest one of the five schemes detailed below the questions.
Low | Criticality of the warehouse to the business |  |  | High
100
Low | Consequences of the loss |  |  | High
50
High | Occupancy |  |  | Low
50
Low | Ceiling height |  |  | High
50
Low | Flammability, fire load and risk of fire spread |  |  | High
50
Low | Probability of ignition |  |  | High
50
Low | Detection challenges (airflows, obstacles, temperature gradient) |  |  | High
50
High | Response capabilities |  |  | Low
50
Low | Provision of automatic suppression (sprinklers) |  |  | High
50
| Total | 500
180 | Between 181 & 360 | Between 361 & 540 | Between 541 & 719 | 720 +
Scheme 1 Ceiling only normal coverage (see table 3) | Scheme 2 Ceiling only strategically positioned relative to the racking | Scheme 3 Ceiling + top of rack detection | Scheme 4 Ceiling + multi-level in rack detection | Scheme 5 Ceiling + localised multi-level in rack
FALSE | FALSE | TRUE | FALSE | FALSE

## Sheet1
WAREHOUSE ASD DESIGN CONSIDERATIONS
The following greyscale table is provided to allow the designer/specifier to consider several questions regarding the overall aspirating detection system design within a warehousing facility. The emphasis and conclusions of the various questions guide the designer/specifier to a selection of five different detection schemes. Scheme 1 to scheme 5 contain increasing amounts of aspirating system detection points to protect the warehouse facility more comprehensively. | [5 empty] | #VALUE!
One of the five boxes underneath each of the highlighted questions may be used to confirm the degree of risk/consideration for the particular warehouse facilty. By way of weighting the results of all the questions should suggest one of the five schemes detailed below the questions. | [6 empty] | Warehouse ASD design consideration comments. At the time of the ASD design it may not be possible to obtain all the correct information or answers to the various questions below and therefore considered assumptions should be made where necessary. It is recommended that these assumptions be recorded with the proposed ASD design for future reference by any interested parties.
Against each of the considerations below enter figures on a scale of 1 to 5 to determine the suggested scheme.
- While integers are expected to be used, this is not mandatory if greater precision is required. - Numbers greater than 5 can be used if a weighting against specific risks is required.
Criticality of the warehouse represents the importance of the warehouse facility to the business. For example, if this is a single warehouse supplying numerous outlets then this is more critical to this business than one which may have multiple warehouses (perhaps regional), which could allow the continuation of supply to the outlets if one warehouse is damaged or lost through fire.
| Low (1) | Criticality of the warehouse to the business |  |  | High (5) | Increasing criticality of facility 1 to 5
0
Consequences of loss represents the effect of the loss of some, or all, of the warehouse facility through fire. How much stock and operational processes are still available to continue to supply products, how long could it take for the restoration of normal supplies, how will the business be able to operate following the fire event, can the business operate following the fire event?
| Low (1) | Consequence of the loss |  |  | High (5) | Increasing consequence of loss 1 to 5
0
Ceiling height can influence how a fire may develop and spread through a warehouse and therefore the resultant amount of stock that could be affected by a fire event. As building height increases, the density and quantity of racking and stored stock generally increases, therefore, an increased fire detection provision may be more appropriate.
| Low (1) | Ceiling Height |  |  | High (5) | 1: h ≤ 10; 2: 10 < h ≤ 15; 3: 15 < h ≤ 20; 4: 20 < h ≤ 25; 5: 25 < h h = height in metres
0
This represents the potential growth of a fire event based on what may be stored in the facility. Increased detection should be considered if the stored stock is flammable, creates a large fire load and permits ease of the fire event spreading quickly. Alternatively, if little fire risk is represented by the stored stock potentially less detection may be required. However, the design should still meet minimum standards.
| Low (1) | Flammability, fire load and risk of fire spread |  |  | High (5) | Increasing risk 1 to 5
0
Probability of ignition represents the likelihood of a fire event happening within the facility. Are there potential ignition sources such as elec./mech. plant, forklift truck or charging areas, are Lithium-Ion batteries used/charged/stored. Is ‘hot working’ allowed? Is there a potential for arson from staff or non-staff? The higher the probability of a fire event would represent the requirement for additional detection.
| Low (1) | Probability of ignition |  |  | High (5) | Increasing probability a fire will start 1 to 5
0
Some facilities may provide detection system challenges. These could include natural and forced airflow changes and airflow movements, temporary or permanent structural or operational obstacles, significant temperature variations, or temperature extremes such as sub-zero cold storage facilities. Detection systems should consider the significance of these factors and be adjusted accordingly.
| Low (1) | Detection challenges (airflows, obstacles, temperature gradient) |  |  | High (5) | Increasing difficulty to detect fire 1 to 5
0
Occupancy represents the availability of staff within the facility (at all times), able to act quickly to a developing fire event. Staff, with access to all areas of the warehouse, could prevent a small fire event becoming a larger one. In automated warehouses there could be very few staff within the facility, making any human intervention unlikely, and thereby increasing the demand for additional automatic detection.
| High (1) | Occupancy |  |  | Low (5) | Higher occupancy offers ability to provide early warning 1 to 5
0
Response capability represents the timeline for a response to a fire event. This can be a facility response by staff to attend a developing fire event, a building fire protection system such as sprinklers, or local fire brigade availability and response. Increased detection may be required if the above are not considered adequate.
| High (1) | Response capabilities |  |  | Low (5) | Ability to respond and fight an incipient fire Full on site fire fighting = 1; No ability to respond on site 5
0
Provision of an automatic fire protection system such as sprinklers should be considered in context of how this extends throughout the storage facility (ceiling level only, in-rack etc.), together with the quantity of stored stock, flammability, fire load, fire risk, and other firefighting responses available to the facility.
| High (1) | Provision of automatic suppression (sprinklers) |  |  | Low (5) | Full sprinkler coverage = 1; No sprinklers = 5
0
| 9 | 10 to 18 | 19 to 27 | 28 to 36 | 37+
| Scheme 1 Ceiling only normal coverage (see table 3) | Scheme 2 Ceiling only strategically positioned relative to the racking | Scheme 3 Ceiling + top of rack detection | Scheme 4 Ceiling + multi-level in rack detection | Scheme 5 Ceiling + localised multi-level in rack | Overall score is given simply by summing inputs. The suggested scheme based on reponses is highlighted in yellow. The bar graph below adds detail to aid the decision - for example if close to boundary perhaps could consider next scheme.
0
OVERALL SCORE